# VOLUME II: ENVIRONMENTAL EXCURSION PROTOCOLS & SAFETY INTERLOCKS

Document ID: NFEC-BOREALIS-VOL2  |  Revision: 2026.4  |  Applies To: Zone-A3 Facilities

# 4.0 ENVIRONMENTAL & CHEMICAL EXCURSION OVERRIDES (TIER 2)

This section defines mandatory component substitutions when operating outside the standard +15°C temperate envelope or when chemical dosing streams introduce incompatible solvents. Per Volume I Section 1.3, all clauses in Section 4.0 strictly SUPERSEDE Volume I Section 2.0 Baseline Schedules.

## 4.1 Thermal Derating & Replacement of Polymer Piping

Although baseline PE-4710 SDR-11 piping (Part #PIPE-HDPE11-STD, Section 2.1) is nominally rated to -40°C under static zero-pressure conditions, dynamic pressurized service (>100 PSI) in Zone-A3 environments (ambient below -35°C) combined with trace hydrocarbon condensate PROHIBITS the use of standard PE-4710 SDR-11 due to rapid crack propagation (RCP) failure risk. All such lines MUST upgrade to Cross-Linked Polyethylene PEX-a SDR-9 Arctic Grade (Part #PIPE-PEX9-ARC) or seamless carbon steel ASTM A333 Grade 6.

## 4.2 Low-Temperature Flange Bolting Override

Baseline ASTM A193 Grade B7 stud bolts (Kit #BOLT-B7-2H, Section 2.3) exhibit rapid Charpy V-notch impact degradation below -29°C. Any flange assembly subject to the Cryogenic Excursion Protocol (Section 4.3) PROHIBITS Grade B7 fasteners and MUST upgrade to Charpy impact-tested ASTM A320 Grade L7 alloy steel stud bolts paired with ASTM A194 Grade 4/L4 heavy hex nuts (Kit #BOLT-L7-L4).

## 4.3 Cryogenic Excursion Protocol Trigger

The Cryogenic Excursion Protocol is automatically triggered for any outdoor assembly located in a zone where the minimum design ambient temperature (MDMT) is below -30°C (including Zone-A3 at -42°C per Section 1.2). Activation of Section 4.3 mandates: (a) Low-temperature bolting per Section 4.2, (b) Thermal piping upgrade per Section 4.1, and (c) Immediate PROHIBITION of baseline Viton FKM-A elastomer seals (Part #SEAL-VT-09, Section 2.2) due to glass-transition embrittlement and seal fracture below -26°C.

## 4.4 Low-Temperature Elastomer Seal Substitution

Whenever baseline Viton seals (Part #SEAL-VT-09) are prohibited by Section 4.3, engineers shall substitute Low-Temperature Fluorosilicone (FVMQ, Part #SEAL-FVMQ-40) inside standard valve body #VLV-200-SS, UNLESS the flow path is classified as a Polar-Solvent Service Line under Section 3.3.

## 4.5 Polar-Solvent & Dual-Excursion Seal Override

Fluorosilicone (FVMQ, Part #SEAL-FVMQ-40) and standard EPDM elastomers experience severe volumetric swell (>45%) and extrusion failure when exposed to anhydrous methanol + trace hydrocarbon mixtures (Section 3.2 / Section 3.3). Therefore, for any flow path subject to BOTH Cryogenic Excursion (Section 4.3) AND Polar-Solvent Service (Section 3.3), Part #SEAL-FVMQ-40 is PROHIBITED. The ONLY approved elastomer is Ultra-Low-Temperature Perfluoroelastomer FFKM (Part #SEAL-FFKM-ULT90). Furthermore, due to the wider gland geometry of #SEAL-FFKM-ULT90, baseline valve body #VLV-200-SS cannot be used; the assembly MUST upgrade to the Cryogenic Trunnion Ball Valve Body (Part #VLV-200-LT).

| Condition / Regime | Trigger Criteria | Prohibited SKUs | Mandated Seal SKU | Mandated Valve SKU |
| --- | --- | --- | --- | --- |
| Temperate Baseline (Sec 2.2) | Ambient >= -15°C, No MeOH | None | SEAL-VT-09 (FKM-A) | VLV-200-SS |
| Cryogenic Only (Sec 4.4) | Ambient < -30°C, No MeOH (Loops A/C) | SEAL-VT-09, BOLT-B7-2H | SEAL-FVMQ-40 (FVMQ) | VLV-200-SS |
| Dual Cryogenic + Polar-Solvent (Sec 4.5) | Ambient < -30°C + MeOH Injection (Loop B) | SEAL-VT-09, SEAL-FVMQ-40, VLV-200-SS | SEAL-FFKM-ULT90 (FFKM) | VLV-200-LT |

# 5.0 ACTIVE SAFETY INTERLOCKS & ACTUATOR SIZING (TIER 3)

Per Volume I Section 1.3, Safety Interlock Directives in Section 5.0 hold Tier 3 precedence and override all Tier 1 and Tier 2 selections.

## 5.1 Stem Breakaway Torque Multiplier for Ultra-Low-Temp FFKM

Empirical cold-box testing confirms that installing Perfluoroelastomer seal Part #SEAL-FFKM-ULT90 inside Cryogenic Trunnion Valve #VLV-200-LT increases valve stem breakaway torque by 185% at -40°C (reaching 215 Nm) compared to baseline Viton seats.

## 5.2 Mandatory Hydraulic Actuator Substitution Directive

Baseline pneumatic rack-and-pinion actuator Part #ACT-PN-100 (Section 2.2) has a maximum output torque of 120 Nm and WILL STALL under emergency shutdown (ESD) demand when paired with #SEAL-FFKM-ULT90 below -30°C. Consequently, whenever Valve #VLV-200-LT is fitted with Seal #SEAL-FFKM-ULT90, Part #ACT-PN-100 is PROHIBITED and the assembly MUST upgrade to High-Torque Spring-Return Hydraulic Actuator Part #ACT-HYD-350 (rated to 400 Nm at -50°C).